## Value Analysis
Installation Value Analysis
Power Installation | Total Hours | Total Days | Total Cost | Total Materials | Total Labor | Est. Crew Size | Estimated Construction Time (Days) | Average IDF Cost | Average IDF Construction Time (Days) | Largest AWG | Smallest AWG | Average AWG | Average Trenching Cost | Average Trenching Time (Hours) | Longest Single IDF Cost (1000ft / 4500ft) | Shortest Single IDF Cost (75ft / 700ft)
Class-4 Indoor | 111.66 | 13.9575 | 49905.66 | 34349.5 | 15556.16 | 2 | 6.9787 | 5999.63 | 0.87687 | 16 | 16 | 16 |  |  | 28099.09 | 11616.98
A/C Indoor | 751.58 | 93.9475 | 68305.16 | 24470.25 | 43834.91 | 5 | 18.7895 | 11401.43 | 3.0805 | 4 | 14 | 8 |  |  | 34882.86 | 13212.25
Class-4 Outdoor | 524.17 | 65.5212 | 205505.08 | 171950 | 33555.08 | 6 | 10.9202 | 17669 | 0.40063 | 16 | 6 | 11 | 6981 | 8.3 | 44354.16 | 22355.03
A/C Outdoor | 1725.39 | 215.6738 | 368074.71 | 256791.32 | 111283.39 | 11 | 19.6067 | 39821 | 1.6136 | 16 | 6 | 11 | 7227.5 | 45 | 110468.59 | 31690.71
Indoor Value Props
Minimum IDF's | 3 | Minimum number of IDFs where FMP provides CapEx benefits
Minimum Distance | 65 feet | Minimum distance from AC power where FMPS provides Time and Cost benefits
Best Distance to use FMPS | 200 feet | This is a target distance for FMP vs AC applications
Power Sweet spot | 1000 watts | This is the load where the (3) channel receiver has the best power to cost ratio
FMPS largest AWG | 16 | This is the AWG size which covers the most scenerios using a single cable
AC largest AWG | 4 | This is the expected cable size for AC power when exceeding 200ft distances
Average Cost Difference | 52.62% | Average cost difference per IDF (includes fixed costs: head end costs, site walk, design and engineering)
Time to Deployment | 37.14% | Significantly less time to deploy FMPS vs traditional power
Outdoor Value Props
Anything Outdoors | 1 | Any devices outside of a building would make sense with FMPS based on cost and time to deployment
Excellent in Difficult Environments | 1 | Any areas where deep trenching is not practical this solution can be run above ground in an approved LV pathway |  |  |  |  | Specialty ¦ Dura-Line (duraline.com) | Duralilne Ariel Duct
Extreme Distances | 3000ft + | Distances beyond 3000 ft requrie extremely large AC cables which can cost upwards of $11/ft
Time Constraints | 50% | FMP can be installed in 50% of the time not even factoring permits and approvals for outdoor trenching
Where is AC a better fit?
Close AC power | 1 | Anywhere that has an electrical panel closer than 50ft
High Power | 4kVA (4500 watts) | Anything above 4kVA will require an AC circtuit - this equates to more power than a fully loaded transmitter chassis and 3 receivers.
Where is Powered Fiber a Better Fit ?
Very low power | <60w | Any application that require lower than 60 watts of power will be better served by class 2
Short Distances | Less than 300ft | Short distances less than 300 feet and less than 800 watts
Special Note | 1 | In most cases the network can be designed so that the Rx acts as a class 2 hub - allowing for a more scalable cost effective design.
As we say FMPS is not vertical specific but challenege specific we mean that the solutions savings are typical of the solution we are providing regardless of the vertical ;for instance if you need to
Add an IDF in a hospital or office or school | it will take you 37% less time and 40 % less cost
Anytime you're running power outside of the building
What is the product / how does it work /
Message to Electrical Contractors | Be more competitive, preserve your margins, free up labor for more profitable projects
Message to integrators, add more scope to your projects, control the project timeline, build better designs
Message to end users control network deployment cost, faster deployment, better network management and resiliance
This is not a vertical focused product but a solutions focused product
Provide power to security cameras | Any Vertical
Provide power to new IDFs | Any Vertical
Centralized UPS | Any Vertical
Interesting cases
Powering a guard shack
Providing USBC
The numbers
Instalaltion Cost | 50%
Installation Time | 75%
Total Capex | 25%
Network Troubleshooting | 15%
What to Ask
Do you need more than 100W of power at that location
Is it less than 4500w total
Is there an electrical Panel within 100ft
Do you have limited pathway space?
Are these extreme distances (more than 3000ft)
Why is it safe
CL4 power didn't exist 5 years ago. Panduit along with other industry experts worked with UL to create the safety standards around this new class of power, and working with NEC creating standards for installation.

## Indoor Installation Full
Indoor Installation Scope
Cost Drivers |  |  |  | Constants
Labor Rates |  |  |  | Installation Assumptions
MEP Design | 207 | per hour |  | Conduit Installation | 6 | ft/hr
Electrician | 72 | per hour |  | Electrical Cable Installation | 15 | ft/hr
Low Voltage Installer | 45 | per hour |  | LV Cable Installation | 110 | ft/hr
Low Voltage Designer | 165 | per hour |  | Trenching | 31 | per foot
|  |  |  | Micro Trenching | 13 | per foot
|  |  |  | Coring | 225 | per core
|  |  |  | Cable Supports | 1 | per 6ft
Pre-Design |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Site Walk / Site Survey | Complete a detailed site walk to review electrical panels in the MDF and IDF locations |  |  |  | 0 | 2 | 90 | 0 | 2 | 90 |  | 90 | 90
Electrical Panel Audit | Complete a full audit of electrical panels and capacity |  |  |  | 0 | 7 | 504 | 0 | 0 | 0 |  | 504 | 0
Sub Total |  |  |  |  | 0 | 9 | 594 | 0 | 2 | 90 | 0 | 594 | 90 | *Requires Building Shutdown
Design |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Power Design | Design a code compliant power system for the MDF and 5 IDF locations |  |  |  | 0 | 11 | 2277 | 0 | 4 | 660 |  | 2277 | 660
Plan Check and Review | Provide plans to AHJ for review and approval |  |  |  | 0 | 48 | 0 | 0 | 0 | 0 |  | 0 | 0
Design Revisions | Assume 1 design revision |  |  |  | 0 | 3 | 621 | 0 | 2 | 330 |  | 621 | 330
Permits | Provide required work permits |  |  |  | 0 | 24 | 2850 | 0 | 0 | 0 |  | 2850 | 0
Sub Total |  |  |  |  | 0 | 86 | 5748 | 0 | 6 | 990 | 0 | 5748 | 990
MDF |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Conduit Installation | Installation of conduit and junction boxes from panel to main rack |  |  |  | 198 | 6 | 432 | 198 | 6 | 432 |  | 630 | 630
Conduit | 3/4 in Conduit | 30 | 1.7 | 51
Receptical | Generic | 2 | 35
Boxes | Generic | 4 | 18 | 72
Misc | Misc | 1 | 75 | 75
Panel Work | Installation of breakers and wiring |  |  |  | 185 | 3 | 216 | 185 | 3 | 216 |  | 401 | 401
Breaker | Generic | 3 | 45 | 135
Wiring | Generic | 1 | 50 | 50
PDU | Install and connect PDU's for equipment connectivity |  |  |  | 900 | 1.5 | 72 | 900 | 1.5 | 72 |  | 972 | 972
PDU Installation | Panduit | 3 | 300 | 900
Cable Installation | Install 10ft #10 AWG Cable |  |  |  | 18 | 2 | 144 | 18 | 2 | 144 |  | 162 | 162
Power Cable | #14 | 30 | 0.6 | 18
FMP Head End | Install Transmitter Chassis, Power Supplies, and Transmitter |  |  |  | 0 | 0 | 0 | 15190 | 10 | 450 |  | 0 | 15640
FMP Head End | Chassis | 2 | 1990 | 3980
FMP Head End | Transmitters | 10 | 725 | 7250
FMP Head End | PSU | 4 | 990 | 3960
Sub Total |  |  |  |  | 1301 | 12.5 | 864 | 16491 | 22.5 | 1314 | 0 | 2165 | 17805
IDF 1 |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install J-Hooks or similar to support Fiber and CL4 Cable |  |  |  | 225 | 30 | 1350 | 225 | 6 | 1350 |  | 1575 | 1575
J-Hooks | Panduit | 50 | 4.5 | 225
Conduit Installation | Installation of conduit and junction boxes from panel to main rack |  |  |  | 254.75 | 12.5 | 900 | 0 | 0 | 0 |  | 1154.75 | 0
Conduit | Generic 3/4 in Conduit | 75 | 1.77 | 132.75
Boxes | Generis | 4 | 18 | 72
Misc | Generic | 1 | 50 | 50
Electrical Panel & Recepticals Recepticals | Install new electrical panel with breakers |  |  |  | 481.77 | 8 | 576 | 0 | 0 | 0 |  | 1057.77 | 0
Panel | Generic | 1 | 355 | 355
Breakers | Generic | 2 | 45 | 90
Conduit | Generic | 1 | 1.77 | 1.77
Receptical | Generic | 1 | 35 | 35
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 588 | 1 | 45 |  | 0 | 633
CL4 Cable | Panduit | 300 | 1.96 | 588
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 225 | 2.7273 | 122.7273 | 225 | 2.7273 | 122.7273 |  | 347.7273 | 347.7273
Fiber Cable | 12-Strand Generic | 300 | 0.35 | 105
Connectors | SM Connector | 24 | 5 | 120
Fiber Cable | 12-Strand Generic | 300 | 0.35 | 105
Connectors | SM Connector | 24 | 5 | 120
Electrical Cable Installation | Install new electrical panel with breakers |  |  |  | 210 | 5 | 360 | 0 | 0 | 0 |  | 570 | 0
Electrical | #8Generic | 75 | 2.8 | 210
FMP Hardwarer | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1650 | 0.25 | 11.25 |  | 0 | 1661.25
Receiver | PRX | 1 | 1650 | 1650
Sub Total |  |  |  |  | 1396.52 | 58.2273 | 3308.7273 | 2688 | 9.9773 | 1528.9773 | 0 | 4705.2473 | 4216.9773
IDF 2 |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install J-Hooks or similar to support Fiber and CL4 Cable |  |  |  | 337.5 | 37 | 1665 | 337.5 | 6 | 1665 |  | 2002.5 | 2002.5
J-Hooks | Panduit | 75 | 4.5 | 337.5
Conduit Installation | Installation of conduit and junction boxes from panel to main rack |  |  |  | 745 | 33.3333 | 2400 | 0 | 0 | 0 |  | 3145 | 0
Conduit | Generic 3/4 in Conduit | 200 | 1.77 | 354
Boxes | Generis | 12 | 18 | 216
Misc | Generic | 1 | 175 | 175
Electrical Panel & Recepticals Recepticals | Install new electrical panel with breakers |  |  |  | 481.77 | 8 | 576 | 0 | 0 | 0 |  | 1057.77 | 0
Panel | Generic | 1 | 355 | 355
Breakers | Generic | 2 | 45 | 90
Conduit | Generic | 1 | 1.77 | 1.77
Receptical | Generic | 1 | 35 | 35
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 882 | 3 | 135 |  | 0 | 1017
CL4 Cable | Panduit | 450 | 1.96 | 882
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 277.5 | 4.0909 | 184.0909 | 277.5 | 4.0909 | 184.0909 |  | 461.5909 | 461.5909
Fiber Cable | 12-Strand Generic | 450 | 0.35 | 157.5
Connectors | SM Connector | 24 | 5 | 120
Fiber Cable | 12-Strand Generic | 450 | 0.35 | 157.5
Connectors | SM Connector | 24 | 5 | 120
Electrical Cable Installation | Install new electrical panel with breakers |  |  |  | 620 | 13.3333 | 600 | 0 | 0 | 0 |  | 1220 | 0
Cable | #6Generic | 200 | 3.1 | 620
FMP Hardwarer | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1650 | 0.25 | 0 |  | 0 | 1650
Receiver | PRX | 1 | 1650 | 1650
Sub Total |  |  |  |  | 2461.77 | 95.7576 | 5425.0909 | 3147 | 13.3409 | 1984.0909 | 0 | 7886.8609 | 5131.0909
IDF 3 |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install J-Hooks or similar to support Fiber and CL4 Cable |  |  |  | 135 | 15 | 675 | 135 | 6 | 675 |  | 810 | 810
J-Hooks | Panduit | 30 | 4.5 | 135
Conduit Installation | Installation of conduit and junction boxes from panel to main rack |  |  |  | 474.15 | 15.8333 | 1140 | 0 | 0 | 0 |  | 1614.15 | 0
Conduit | Generic 3/4 in Conduit | 95 | 1.77 | 168.15
Boxes | Generis | 12 | 18 | 216
Misc | Generic | 1 | 90 | 90
Electrical Panel & Recepticals Recepticals | Install new electrical panel with breakers |  |  |  | 481.77 | 8 | 576 | 0 | 0 | 0 |  | 1057.77 | 0
Panel | Generic | 1 | 355 | 355
Breakers | Generic | 2 | 45 | 90
Conduit | Generic | 1 | 1.77 | 1.77
Receptical | Generic | 1 | 35 | 35
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 392 | 3 | 135 |  | 0 | 527
CL4 Cable | Panduit | 200 | 1.96 | 392
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 190 | 1.8182 | 81.8182 | 190 | 1.8182 | 81.8182 |  | 271.8182 | 271.8182
Fiber Cable | 12-Strand Generic | 200 | 0.35 | 70
Connectors | SM Connector | 24 | 5 | 120
Fiber Cable | 12-Strand Generic | 200 | 0.35 | 70
Connectors | SM Connector | 24 | 5 | 120
Electrical Cable Installation | Install new electrical panel with breakers |  |  |  | 251.75 | 6.3333 | 285 | 0 | 0 | 0 |  | 536.75 | 0
Cable | #12 Generic | 95 | 2.65 | 251.75
FMP Hardwarer | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1650 | 0.25 | 0 |  | 0 | 1650
Receiver | PRX | 1 | 1650 | 1650
Sub Total |  |  |  |  | 1532.67 | 46.9848 | 2757.8182 | 2367 | 11.0682 | 891.8182 | 0 | 4290.4882 | 3258.8182
IDF 4 |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install J-Hooks or similar to support Fiber and CL4 Cable |  |  |  | 675 | 70 | 3150 | 675 | 6 | 3150 |  | 3825 | 3825
J-Hooks | Panduit | 150 | 4.5 | 675
Conduit Installation | Installation of conduit and junction boxes from panel to main rack |  |  |  | 1855.25 | 54.1667 | 3900 | 0 | 0 | 0 |  | 5755.25 | 0
Conduit | Generic 3/4 in Conduit | 325 | 1.77 | 575.25
Boxes | Generis | 35 | 18 | 630
Misc | Generic | 1 | 650 | 650
Electrical Panel & Recepticals Recepticals | Install new electrical panel with breakers |  |  |  | 481.77 | 8 | 576 | 0 | 0 | 0 |  | 1057.77 | 0
Panel | Generic | 1 | 355 | 355
Breakers | Generic | 2 | 45 | 90
Conduit | Generic | 1 | 1.77 | 1.77
Receptical | Generic | 1 | 35 | 35
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1764 | 3 | 135 |  | 0 | 1899
CL4 Cable | Panduit | 900 | 1.96 | 1764
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 435 | 8.1818 | 368.1818 | 435 | 8.1818 | 368.1818 |  | 803.1818 | 803.1818
Fiber Cable | 12-Strand Generic | 900 | 0.35 | 315
Connectors | SM Connector | 24 | 5 | 120
Fiber Cable | 12-Strand Generic | 900 | 0.35 | 315
Connectors | SM Connector | 24 | 5 | 120
Electrical Cable Installation | Install new electrical panel with breakers |  |  |  | 1332.5 | 21.6667 | 975 | 0 | 0 | 0 |  | 2307.5 | 0
Cable | #4 Generic | 325 | 4.1 | 1332.5
FMP Hardwarer | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1650 | 0.25 | 0 |  | 0 | 1650
Receiver | PRX | 1 | 1650 | 1650
Sub Total |  |  |  |  | 4779.52 | 162.0152 | 8969.1818 | 4524 | 17.4318 | 3653.1818 | 0 | 13748.7018 | 8177.1818
IDF 5 |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install J-Hooks or similar to support Fiber and CL4 Cable |  |  |  | 765 | 85 | 3825 | 765 | 6 | 3825 |  | 4590 | 4590
J-Hooks | Panduit | 170 | 4.5 | 765
Conduit Installation | Installation of conduit and junction boxes from panel to main rack |  |  |  | 4806 | 100 | 7200 | 0 | 0 | 0 |  | 12006 | 0
Conduit | Generic 3/4 in Conduit | 600 | 1.77 | 1062
Boxes | Generis | 83 | 18 | 1494
Misc | Generic | 1 | 2250 | 2250
Electrical Panel & Recepticals Recepticals | Install new electrical panel with breakers |  |  |  | 1832.77 | 19 | 1368 | 0 | 0 | 0 |  | 3200.77 | 0
Panel | Generic | 2 | 355 | 710
Breakers | Generic | 2 | 45 | 90
Conduit | Generic | 1 | 1.77 | 1.77
Transformer | Generic | 2 | 498 | 996
Receptical | Generic | 1 | 35 | 35
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1960 | 3 | 135 |  | 0 | 2095
CL4 Cable | Panduit | 1000 | 1.96 | 1960
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 470 | 9.0909 | 409.0909 | 470 | 9.0909 | 409.0909 |  | 879.0909 | 879.0909
Fiber Cable | 12-Strand Generic | 1000 | 0.35 | 350
Connectors | SM Connector | 24 | 5 | 120
Fiber Cable | 12-Strand Generic | 1000 | 0.35 | 350
Connectors | SM Connector | 24 | 5 | 120
Electrical Cable Installation | Install new electrical panel with breakers |  |  |  | 3900 | 40 | 1800 | 0 | 0 | 0 |  | 5700 | 0
Cable | #1 Generic | 600 | 6.5 | 3900
FMP Hardwarer | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1650 | 0.25 | 0 |  | 0 | 1650
Receiver | PRX | 1 | 1650 | 1650
Sub Total |  |  |  |  | 11773.77 | 253.0909 | 14602.0909 | 4845 | 18.3409 | 4369.0909 | 0 | 26375.8609 | 9214.0909
General |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Cable Management | General cable management and slack management |  |  |  | 1000 | 6 | 270 | 250 | 6 | 270 |  | 1270 | 520
Misc | Panduit | 1 | 1000 | 1000
Misc | Panduit | 1 | 250 | 250
Labeling | Labeling of all cables |  |  |  | 225 | 15 | 675 | 37.5 | 3 | 135 |  | 900 | 172.5
Labels | Panduit | 300 | 0.75 | 225
Labels | Panduit | 50 | 0.75 | 37.5
Documentation | Provide asbuilt drawings |  |  |  | 0 | 3 | 621 | 0 | 2 | 330 |  | 621 | 330
0
0
Inspections | Assist with required inspections and onsite review |  |  |  | 0 | 4 |  | 0 | 0 | 0 |  | 0 | 0
0
0
Sub Total |  |  |  |  | 1225 | 28 | 1566 | 287.5 | 11 | 735 | 0 | 2791 | 1022.5
|  |  |  | Grand Total | 24470.25 | 751.5758 | 43834.9091 | 34349.5 | 111.6591 | 15556.1591 | 0 | 68305.1591 | 49905.6591
Scenerio: Expansion of building connectivity network to 5 new IDF locations
- Mix of distances (all distances are over 50ft, anything under 50ft doesnt make sense)
- Designed to use the maximum amount of FMP equipment with minimal output power to simulate a worst case scenerio
- un optimized design
Location: Central US MDF: Power Available
Distance from MDF / Closest AC Power / Capacity Needed
IDF 1 300 / 75 / 1000
IDF 2 450 / 200 / 1000
IDF 3 250 / 95 / 1000
IDF 4 900 / 325 / 1000
IDF 5 1000 / 600 / 1000

## Outdoor Installation
Outdoor Installation Scope
Cost Drivers |  |  |  | Constants
Labor Rates |  |  |  | Installation Assumptions
MEP Design | 207 | per hour |  | Conduit Installation | 6 | ft/hr
Electrician | 72 | per hour |  | Electrical Cable Installation | 30 | ft/hr
Low Voltage Installer | 45 | per hour |  | LV Cable Installation | 110 | ft/hr
Low Voltage Designer | 165 | per hour |  | Trenching | 50 | ft/hr | includes backfill
Trenching Labor | 55 | per hour |  | Micro Trenching | 300 | ft/hr
Micro Trenching | 92 | per hour |  | Coring | 225 | per core
|  |  |  | Cable Supports | 1 | per 6ft
Directional Boring
Pre-Design |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Site Walk / Site Survey | Complete a detailed site walk to review electrical panels in the MDF and IDF locations |  |  |  | 0 | 8 | 360 | 0 | 8 | 360 |  | 360 | 360
Electrical Panel Audit | Complete a full audit of electrical panels and capacity |  |  |  | 0 | 4 | 288 | 0 | 0 | 0 |  | 288 | 0
Sub Total |  |  |  |  | 0 | 12 | 648 | 0 | 8 | 360 | 0 | 648 | 360 | *Requires Building Shutdown
Design |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Power Design | Design a code compliant power system for the MDF and 4 IDF locations |  |  |  | 0 | 20 | 4140 | 0 | 4 | 660 |  | 4140 | 660
Plan Check and Review | Provide plans to AHJ for review and approval |  |  |  | 0 | 48 | 0 | 0 | 48 | 0 |  | 0 | 0
Design Revisions | Assume 1 design revision |  |  |  | 0 | 8 | 1656 | 0 | 4 | 660 |  | 1656 | 660
Permits | Provide required work permits |  |  |  | 0 | 24 | 6500 | 0 | 0 | 3850 |  | 6500 | 3850
Sub Total |  |  |  |  | 0 | 100 | 12296 | 0 | 56 | 5170 | 0 | 12296 | 5170
MDF |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Conduit Installation | Installation of conduit and junction boxes from panel to main rack |  |  |  | 995 | 20 | 1440 | 0 | 0 | 0 |  | 2435 | 0
Conduit | 1 in | 100 | 1.7 | 170
Receptical | Generic | 2 | 35 | 70
Boxes | Generic | 10 | 18 | 180
Misc | Misc | 1 | 575 | 575
Panel Work | Installation of breakers and wiring |  |  |  | 3825 | 10 | 720 | 475 | 4 | 720 |  | 4545 | 1195
Breaker | Generic | 5 | 45 | 225
Wiring | Generic | 5 | 50 | 250
Indoor Transformer | Generic | 1 | 3350 | 3350
PDU | Install and connect PDU's for equipment connectivity |  |  |  | 600 | 1.5 | 72 | 600 | 1.5 | 72 |  | 672 | 672
PDU Installation | Panduit | 2 | 300 | 600
Cable Installation | Install new electrical panel with breakers |  |  |  | 545 | 8.9091 | 400.9091 | 295 | 3 | 135 |  | 945.9091 | 430
Fiber Cable | 12-Strand Generic I/O | 100 | 0.7 | 70
Power Cable | 6AWG | 100 | 4.75 | 475
Fiber Cable | 12-Strand Generic | 100 | 0.7 | 70
FMPS | 16AWG I/O | 100 | 2.25 | 225
Lightning Protection | Install lighting protection at building entrance point |  |  |  | 455 | 4 | 288 | 2970 | 5 | 225 |  | 743 | 3195
Building Entrance Panel | Outdoor Service Entrance Panel | 1 | 455 | 455
DC SPD | Generic | 15 | 198 | 2970
FMP Head End | Install Transmitter Chassis, Power Supplies, and Transmitter |  |  |  | 0 | 0 | 0 | 5155 | 9 | 405 |  | 0 | 5560
FMP Head End | Chassis | 1 | 1990 | 1990
FMP Head End | Transmitters | 3 | 725 | 2175
FMP Head End | PSU | 1 | 990 | 990
Sub Total |  |  |  |  | 6420 | 44.4091 | 2920.9091 | 9495 | 22.5 | 1557 | 0 | 9340.9091 | 11052
Annex Building (IDF) |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install low voltage 2 duct conduit system (Micro Trench) |  |  |  | 4875 | 6.5 | 598 | 4875 | 6.5 | 598 |  | 5473 | 5473
LV Flex Conduit | Generic 2 duct flex | 1950 | 0.4 | 780
Backfill | Generic | 1950 | 2.1 | 4095
Class 1 Electrical Pathway | Installation of conduit and junction boxes from panel to main rack |  |  |  | 4561.5 | 39 | 2808 | 0 | 0 | 0 |  | 7369.5 | 0
Conduit | Generic 2in Sch 40 | 1950 | 1.77 | 3451.5
Handholds | Generis | 20 | 18 | 360
Misc | Generic | 1 | 750 | 750
Electrical Panel & Recepticals Recepticals | Install new electrical panel with breakers |  |  |  | 1338.85 | 6 | 432 | 0 | 0 | 0 |  | 1770.85 | 0
Transformer | Generic | 1 | 1250 | 1250
SPD | Generic | 1 | 45 | 45
Conduit | Generic | 5 | 1.77 | 8.85
Receptical | Generic | 1 | 35 | 35
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 8775 | 6 | 270 |  | 0 | 9045
CL4 Cable | Panduit | 3900 | 2.25 | 8775
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 802.5 | 17.7273 | 797.7273 | 802.5 | 17.7273 | 797.7273 |  | 1600.2273 | 1600.2273
Fiber Cable | 12-Strand Generic | 1950 | 0.35 | 682.5
Connectors | SM Connector | 24 | 5 | 120
Fiber Cable | 12-Strand Generic | 1950 | 0.35 | 682.5
Connectors | SM Connector | 24 | 5 | 120
Electrical Cable Installation | Install new electrical panel with breakers |  |  |  | 9262.5 | 65 | 2925 | 0 | 0 | 0 |  | 12187.5 | 0
Electrical | #6Generic | 1950 | 4.75 | 9262.5
FMP Hardwarer | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 3300 | 0.25 | 11.25 |  | 0 | 3311.25
Receiver | PRX | 2 | 1650 | 3300
Sub Total |  |  |  |  | 20840.35 | 134.2273 | 7560.7273 | 17752.5 | 30.4773 | 1676.9773 | 0 | 28401.0773 | 19429.4773
Parking Garage A - Camera Switch |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install low voltage 2 duct conduit system (Micro Trench) |  |  |  | 1750 | 2.3333 | 214.6667 | 1750 | 2.3 | 214.6667 |  | 1964.6667 | 1964.6667
LV Flex Conduit | Generic 2 duct flex | 700 | 0.4 | 280
Backfill | Generic | 700 | 2.1 | 1470
Conduit Installation | Installation of conduit and junction boxes from panel to main rack |  |  |  | 1504 | 14 | 1008 | 0 | 0 | 0 |  | 2512 | 0
Conduit | Generic 2in Sch 40 | 700 | 1.77 | 1239
Boxes | Generis | 5 | 18 | 90
Misc | Generic | 1 | 175 | 175
Electrical Panel & Recepticals Recepticals | Install new electrical panel with breakers |  |  |  | 481.77 | 8 | 576 | 0 | 0 | 0 |  | 1057.77 | 0
Panel | Generic | 1 | 355 | 355
Breakers | Generic | 2 | 45 | 90
Conduit | Generic | 1 | 1.77 | 1.77
Receptical | Generic | 1 | 35 | 35
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1372 | 3 | 135 |  | 0 | 1507
CL4 Cable | Panduit | 700 | 1.96 | 1372
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 365 | 6.3636 | 286.3636 | 365 | 6.3636 | 286.3636 |  | 651.3636 | 651.3636
Fiber Cable | 12-Strand Generic | 700 | 0.35 | 245
Connectors | SM Connector | 24 | 5 | 120
Fiber Cable | 12-Strand Generic | 700 | 0.35 | 245
Connectors | SM Connector | 24 | 5 | 120
Electrical Cable Installation | Install new electrical panel with breakers |  |  |  | 2170 | 23.3333 | 1050 | 0 | 0 | 0 |  | 3220 | 0
Cable | #6Generic | 700 | 3.1 | 2170
FMP Hardwarer | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1650 | 0.25 | 0 |  | 0 | 1650
Receiver | PRX | 1 | 1650 | 1650
Sub Total |  |  |  |  | 6270.77 | 54.0303 | 3135.0303 | 5137 | 11.9136 | 636.0303 | 0 | 9405.8003 | 5773.0303
Jogging Path - Emergency Phone |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install low voltage 2 duct conduit system (Micro Trench) |  |  |  | 7000 | 9.3333 | 858.6667 | 7000 | 9.33 | 858.6667 |  | 7858.6667 | 7858.6667
LV Flex Conduit | Generic 2 duct flex | 2800 | 0.4 | 1120
Backfill | Generic | 2800 | 2.1 | 5880
Conduit Installation | Installation of conduit and junction boxes from panel to main rack |  |  |  | 5221 | 56 | 4032 | 0 | 0 | 0 |  | 9253 | 0
Conduit | Generic 2in Sch 40 | 2800 | 1.77 | 4956
Boxes | Generis | 5 | 18 | 90
Misc | Generic | 1 | 175 | 175
Electrical Panel & Recepticals Recepticals | Install new electrical panel with breakers |  |  |  | 481.77 | 8 | 576 | 0 | 0 | 0 |  | 1057.77 | 0
Panel | Generic | 1 | 355 | 355
Breakers | Generic | 2 | 45 | 90
Conduit | Generic | 1 | 1.77 | 1.77
Receptical | Generic | 1 | 35 | 35
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 5488 | 10 | 450 |  | 0 | 5938
CL4 Cable | Panduit | 2800 | 1.96 | 5488
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 1100 | 25.4545 | 1145.4545 | 1100 | 25.4545 | 1145.4545 |  | 2245.4545 | 2245.4545
Fiber Cable | 12-Strand Generic | 2800 | 0.35 | 980
Connectors | SM Connector | 24 | 5 | 120
Fiber Cable | 12-Strand Generic | 2800 | 0.35 | 980
Connectors | SM Connector | 24 | 5 | 120
Electrical Cable Installation | Install new electrical panel with breakers |  |  |  | 8680 | 93.3333 | 4200 | 0 | 0 | 0 |  | 12880 | 0
Cable | #6Generic | 2800 | 3.1 | 8680
FMP Hardwarer | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1650 | 0.25 | 11.25 |  | 0 | 1661.25
Receiver | PRX | 1 | 1650 | 1650
Sub Total |  |  |  |  | 22482.77 | 192.1212 | 10812.1212 | 15238 | 45.0345 | 2465.3712 | 0 | 33294.8912 | 17703.3712
North Parking Lot - Power Distribution |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install low voltage 2 duct conduit system (Micro Trench) |  |  |  | 11250 | 15 | 1380 | 11250 | 15 | 1380 |  | 12630 | 12630
LV Flex Conduit | Generic 2 duct flex | 4500 | 0.4 | 1800
Backfill | Generic | 4500 | 2.1 | 9450
Conduit Installation | Installation of conduit and junction boxes from panel to main rack |  |  |  | 8230 | 90 | 6480 | 0 | 0 | 0 |  | 14710 | 0
Conduit | Generic 2in Sch 40 | 4500 | 1.77 | 7965
Boxes | Generis | 5 | 18 | 90
Misc | Generic | 1 | 175 | 175
Electrical Panel & Recepticals Recepticals | Install new electrical panel with breakers |  |  |  | 481.77 | 8 | 576 | 0 | 0 | 0 |  | 1057.77 | 0
Panel | Generic | 1 | 355 | 355
Breakers | Generic | 2 | 45 | 90
Conduit | Generic | 1 | 1.77 | 1.77
Receptical | Generic | 1 | 35 | 35
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 8820 | 25 | 1125 |  | 0 | 9945
CL4 Cable | Panduit | 4500 | 1.96 | 8820
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 1695 | 40.9091 | 1840.9091 | 1695 | 40.9091 | 1840.9091 |  | 3535.9091 | 3535.9091
Fiber Cable | 12-Strand Generic | 4500 | 0.35 | 1575
Connectors | SM Connector | 24 | 5 | 120
Fiber Cable | 12-Strand Generic | 4500 | 0.35 | 1575
Connectors | SM Connector | 24 | 5 | 120
Electrical Cable Installation | Install new electrical panel with breakers |  |  |  | 49500 | 150 | 6750 | 0 | 0 | 0 |  | 56250 | 0
Cable | #2Generic | 4500 | 11 | 49500
FMP Hardwarer | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1650 | 0.25 | 11.25 |  | 0 | 1661.25
Receiver | PRX | 1 | 1650 | 1650
Sub Total |  |  |  |  | 71156.77 | 303.9091 | 17026.9091 | 23415 | 81.1591 | 4357.1591 | 0 | 88183.6791 | 27772.1591
General |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Cable Management | General cable management and slack management |  |  |  | 1000 | 6 | 270 | 250 | 6 | 270 |  | 1270 | 520
Misc | Panduit | 1 | 1000 | 1000
Misc | Panduit | 1 | 250 | 250
Labeling | Labeling of all cables |  |  |  | 225 | 15 | 675 | 37.5 | 3 | 135 |  | 900 | 172.5
Labels | Panduit | 300 | 0.75 | 225
Labels | Panduit | 50 | 0.75 | 37.5
Documentation | Provide asbuilt drawings |  |  |  | 0 | 3 | 621 | 0 | 2 | 330 |  | 621 | 330
0
0
Inspections | Assist with required inspections and onsite review |  |  |  | 0 | 4 |  | 0 | 0 | 0 |  | 0 | 0
0
0
Sub Total |  |  |  |  | 1225 | 28 | 1566 | 287.5 | 11 | 735 | 0 | 2791 | 1022.5
|  |  |  | Grand Total | 128395.66 | 856.697 | 55317.697 | 71325 | 258.0845 | 16597.5379 | 0 | 183713.357 | 87922.5379
Scenerio: Adding security devices to the network
- Mix of distances - significant that would be cost prohibitive
- Designed for maximum reach
- all outdoor applications originating from a single building
Location: Central US MDF: Power Available - incluides all cable and equipment to the building entry point approx 100ft to building egress.
Distance from MDF / Capacity Needed
Annex Building IDF 1950 / 3000
Security Camera Switch -Parking Garage A 750 / 400
Jogging Path Emergency Phone 2800/ 250
North Parking Lost (w/ CL2 Distribution) 4500 / 1000

## Outdoor vs Class 2
Mixed vs Class 2
Cost Drivers |  |  |  | Constants
Labor Rates |  |  |  | Installation Assumptions
MEP Design | 207 | per hour |  | Conduit Installation | 6 | ft/hr
Electrician | 72 | per hour |  | Electrical Cable Installation | 30 | ft/hr
Low Voltage Installer | 45 | per hour |  | LV Cable Installation | 110 | ft/hr
Low Voltage Designer | 165 | per hour |  | Trenching | 50 | ft/hr | includes backfill
Trenching Labor | 55 | per hour |  | Micro Trenching | 300 | ft/hr
Micro Trenching | 92 | per hour |  | Coring | 225 | per core
|  |  |  | Cable Supports | 1 | per 6ft
Directional Boring
Pre-Design |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Site Walk / Site Survey | Complete a detailed site walk to review electrical panels in the MDF and IDF locations |  |  |  | 0 | 8 | 360 | 0 | 8 | 360 |  | 360 | 360
Electrical Panel Audit | Complete a full audit of electrical panels and capacity |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Sub Total |  |  |  |  | 0 | 8 | 360 | 0 | 8 | 360 | 0 | 360 | 360 | *Requires Building Shutdown
Design |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Power Design | Design a code compliant power system for the MDF and 5 IDF locations |  |  |  | 0 | 8 | 1656 | 0 | 8 | 1320 |  | 1656 | 1320
Plan Check and Review | Provide plans to AHJ for review and approval |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Design Revisions | Assume 1 design revision |  |  |  | 0 | 4 | 660 | 0 | 4 | 660 |  | 660 | 660
Permits | Provide required work permits |  |  |  | 0 | 0 | 2500 | 0 | 0 | 2500 |  | 2500 | 2500
Sub Total |  |  |  |  | 0 | 12 | 4816 | 0 | 12 | 4480 | 0 | 4816 | 4480
MDF |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Conduit Installation | Installation of conduit and junction boxes from panel to main rack |  |  |  | 265 | 9 | 648 | 265 | 9 | 648 |  | 913 | 913
Conduit | 1 in | 20 | 1.7 | 34
Receptical | Generic | 2 | 35 | 70
Boxes | Generic | 2 | 18 | 36
Misc | Misc | 1 | 125 | 125
Panel Work | Installation of breakers and wiring |  |  |  | 285 | 6 | 432 | 285 | 6 | 432 |  | 717 | 717
Breaker | Generic | 3 | 45 | 135
Wiring | Generic | 3 | 50 | 150
PDU | Install and connect PDU's for equipment connectivity |  |  |  | 600 | 1.5 | 72 | 600 | 1.5 | 72 |  | 672 | 672
PDU Installation | Panduit | 2 | 300 | 600
Lightning Protection | Install lighting protection at building entrance point |  |  |  | 1530 | 8 | 576 | 360 | 2 | 90 |  | 2106 | 450
DC SPD | Generic | 17 | 90 | 1530
DC SPD | Generic | 4 | 90 | 360
Head End Power Equipment | Install Transmitter Chassis, Power Supplies, and Transmitter |  |  |  | 28292 | 5 | 225 | 9820 | 2 | 90 |  | 28517 | 9910
Power Supply | Berk | 5 | 899 | 4495
Power Transmitter | Berk | 8 | 2150 | 17200
Chassis | Berk | 3 | 2199 | 6597
FMP Head End | Chassis | 1 | 1990 | 1990
FMP Head End | Transmitters | 4 | 725 | 2900
FMP Head End | PSU | 2 | 990 | 1980
Media Converter | Generic - Modular - 4 port | 1 | 2950 | 2950
Sub Total |  |  |  |  | 30972 | 29.5 | 1953 | 11330 | 20.5 | 1332 | 0 | 32925 | 12662
Annex Building (500watts) Existing Pathway |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install low voltage 2 duct conduit system (Micro Trench) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
LV Flex Conduit | Generic 2 duct flex | 0 | 0 | 0
Backfill | Generic | 0 | 0 | 0
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 663.75 | 1 | 45 |  | 0 | 708.75
CL4 Cable | Panduit | 295 | 2.25 | 663.75
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 2578.3 | 2.6818 | 120.6818 | 223.25 | 6 | 270 |  | 2698.9818 | 493.25
Composite Cable | 4C-8f | 295 | 5.75 | 1696.25
Composite Cable | 2C-2f | 295 | 2.99 | 882.05
Fiber Cable | 12-Strand Generic | 295 | 0.35 | 103.25
Connectors | SM Connector | 24 | 5 | 120
Lightning Protection | Install lightning protection at the end device location |  |  |  | 270 | 4 | 180 | 270 | 3 | 135 |  | 450 | 405
DC SPD | Generic | 5 | 90 | 450
DC SPD | Generic | 3 | 90 | 270
Remote Side Hardware | Install new electrical panel with breakers |  |  |  | 2197 | 2 | 90 | 2025 | 3 | 135 |  | 2287 | 2160
Media Converter 4P | Berk | 2 | 899 | 1798
Media Converter 2P | Berk | 1 | 399 | 399
Receiver | PRX | 1 | 1650 | 1650
Media Converter | Generic - 4PoE | 1 | 375 | 375
Sub Total |  |  |  |  | 5045.3 | 8.6818 | 390.6818 | 3182 | 13 | 585 | 0 | 5435.9818 | 3767
Parking Garage A (400watts) Security Camera |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install low voltage 2 duct conduit system (Micro Trench) |  |  |  | 412.5 | 15 | 1380 | 412.5 | 15 | 1380 |  | 1792.5 | 1792.5
J-Hooks | Panduit | 75 | 5.5 | 412.5
LV Flex Conduit | Generic 2 duct flex | 0 | 0 | 0
Backfill | Generic | 0 | 0 | 0
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 1687.5 | 1.1 | 0 |  | 0 | 1687.5
CL4 Cable | Panduit | 750 | 2.25 | 1687.5
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 8625 | 13.6364 | 613.6364 | 382.5 | 12.5 | 562.5 |  | 9238.6364 | 945
Composite Cable | 4C-8f | 1500 | 5.75 | 8625
Fiber Cable | 12-Strand Generic | 750 | 0.35 | 262.5
Connectors | SM Connector | 24 | 5 | 120
Lightning Protection | Install lightning protection at the end device location |  |  |  | 270 | 4 | 180 | 270 | 3 | 135 |  | 450 | 405
DC SPD | Generic | 4 | 90 | 360
DC SPD | Generic | 3 | 90 | 270
Remote Side Hardware | Install new electrical panel with breakers |  |  |  | 1798 | 3 | 135 | 2025 | 3 | 0 |  | 1933 | 2025
Media Converter 4P | Berk | 2 | 899 | 1798
Receiver | PRX | 1 | 1650 | 1650
Media Converter | Generic - 4PoE | 1 | 375 | 375
Sub Total |  |  |  |  | 11105.5 | 35.6364 | 2308.6364 | 4777.5 | 34.6 | 2077.5 | 0 | 13414.1364 | 6855
Jogging Path Emergency Phone (250watts) |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install low voltage 2 duct conduit system (Micro Trench) |  |  |  | 3500 | 4.6667 | 429.3333 | 3500 | 4.7 | 429.3333 |  | 3929.3333 | 3929.3333
LV Flex Conduit | Generic 2 duct flex | 1400 | 0.4 | 560
Backfill | Generic | 1400 | 2.1 | 2940
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 3150 | 3 | 135 |  | 0 | 3285
CL4 Cable | Panduit | 1400 | 2.25 | 3150
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 12236 | 12.7273 | 572.7273 | 610 | 16 | 720 |  | 12808.7273 | 1330
Composite Cable | 4C-8f | 1400 | 5.75 | 8050
Composite Cable | 2C-2f | 1400 | 2.99 | 4186
Fiber Cable | 12-Strand Generic | 1400 | 0.35 | 490
Connectors | SM Connector | 24 | 5 | 120
Lightning Protection | Install lightning protection at the end device location |  |  |  | 270 | 4 | 180 | 270 | 3 | 135 |  | 450 | 405
DC SPD | Generic | 3 | 90 | 270
DC SPD | Generic | 3 | 90 | 270
Remote Side Hardware | Install new electrical panel with breakers |  |  |  | 1298 | 3 | 135 | 2025 | 3 | 135 |  | 1433 | 2160
Media Converter 4P | Berk | 1 | 899 | 899
Media Converter 2P | Berk | 1 | 399 | 399
Receiver | PRX | 1 | 1650 | 1650
Media Converter | Generic - 4PoE | 1 | 375 | 375
Sub Total |  |  |  |  | 17304 | 24.3939 | 1317.0606 | 9555 | 29.7 | 1554.3333 | 0 | 18621.0606 | 11109.3333
North Parking Lot (200watts) |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
LV Pathway Installation | Install low voltage 2 duct conduit system (Micro Trench) |  |  |  | 7000 | 9.3333 | 858.6667 | 7000 | 9.3 | 858.6667 |  | 7858.6667 | 7858.6667
LV Flex Conduit | Generic 2 duct flex | 2800 | 0.4 | 1120
Backfill | Generic | 2800 | 2.1 | 5880
CL4 Cable Installation | Install new electrical panel with breakers |  |  |  | 0 | 0 | 0 | 6300 | 5 | 225 |  | 0 | 6525
CL4 Cable | Panduit | 2800 | 2.25 | 6300
Fiber Cable Installation | Install new electrical panel with breakers |  |  |  | 24472 | 25.4545 | 1145.4545 | 1100 | 30 | 1350 |  | 25617.4545 | 2450
Composite Cable | 4C-8f | 2800 | 5.75 | 16100
Composite Cable | 2C-2f | 2800 | 2.99 | 8372
Fiber Cable | 12-Strand Generic | 2800 | 0.35 | 980
Connectors | SM Connector | 24 | 5 | 120
Lightning Protection | Install lightning protection at the end device location |  |  |  | 270 | 3 | 135 | 270 | 3 | 135 |  | 405 | 405
DC SPD | Generic | 3 | 90 | 270
DC SPD | Generic | 3 | 90 | 270
Remote Side Hardware | Install new electrical panel with breakers |  |  |  | 899 | 3 | 135 | 2025 | 3 | 135 |  | 1034 | 2160
Media Converter 4P | Berk | 1 | 899 | 899
Receiver | PRX | 1 | 1650 | 1650
Media Converter | Generic - 4PoE | 1 | 375 | 375
Sub Total |  |  |  |  | 32641 | 40.7879 | 2274.1212 | 16695 | 50.3 | 2703.6667 | 0 | 34915.1212 | 19398.6667
General |  |  |  |  | Materials (AC) | Hours (AC) | Labor Cost (AC) | Materials (CL4) | Hours (CL4) | Labor Cost (CL4) |  | Total (AC) | Total (CL4)
Cable Management | General cable management and slack management |  |  |  | 2400 | 6 | 270 | 800 | 6 | 270 |  | 2670 | 1070
Misc | Panduit | 24 | 100 | 2400
Misc | Panduit | 8 | 100 | 800
Labeling | Labeling of all cables |  |  |  | 225 | 15 | 675 | 75 | 3 | 135 |  | 900 | 210
Labels | Panduit | 300 | 0.75 | 225
Labels | Panduit | 100 | 0.75 | 75
Documentation | Provide asbuilt drawings |  |  |  | 0 | 7 | 1449 | 0 | 2 | 330 |  | 1449 | 330
0
0
Inspections | Assist with required inspections and onsite review |  |  |  | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0
0
0
Sub Total |  |  |  |  | 2625 | 28 | 2394 | 875 | 11 | 735 | 0 | 5019 | 1610
|  |  |  | Grand Total | 99692.8 | 187 | 15813.5 | 46414.5 | 179.1 | 13827.5 | 0 | 115506.3 | 60242
[12 empty] | 28876.575 | 15060.5
0.52155
Scenerio: Adding security devices to the network against conventional class2 power
- Mix of distances - significant that would be cost prohibitive along with some short mixed environment applications
- Designed within the maximum power and distance limitations of powered fiber
- all outdoor applications originating from a single building
Location: Central US MDF: Power Available - incluides all cable and equipment to the building entry point
Distance from MDF / Capacity Needed
Annex Building IDF 295 / 500 - path existing
Security Camera Switch -Parking Garage A 750 / 400 - free air install
Jogging Path Emergency Phone 1400/ 250
North Parking Lost (Direct to devices) 2800 / 200

## Materials Pricing
*Not Validated
Category | Part Type | Part Manufacturer | Part Number | Part Description | Quantity | Unit Price | Extended Price
FMP Head End | Chassis |  |  |  | 2 | 1990 | 3980
FMP Head End | Transmitters |  |  |  | 15 | 725 | 10875
FMP Head End | PSU |  |  |  | 5 | 960 | 4800
Category | Part Type | Part Manufacturer | Part Number | Part Description | Quantity | Unit Price | Extended Price
FMP IDF | Receiver |  |  |  | 1 | 1650
Category | Part Type | Part Manufacturer | Part Number | Part Description | Quantity | Unit Price | Extended Price
FMP Cable | Indoor |  |  |  | 1 | 1.46
FMP Cable | Indoor/Outdoor |  |  |  | 1 | 2.06
Category | Part Type | Part Manufacturer | Part Number | Part Description | Quantity | Unit Price | Extended Price
AC Panel | Breaker |  |  |  | 1 | 95
AC Panel | Panel |  |  |  | 1 | 364
AC Transformer | Indoor Transformer (10KVA) |  |  |  | 1 | 3350
AC Transformer | Outdoor Transformer |  |  |  | 1 | 823
Category | Part Type | Part Manufacturer | Part Number | Part Description | Quantity | Unit Price | Extended Price
AC Pathway | Conduit 1in |  |  |  | 1 | 1.07
AC Pathway | Conduit 1.5in |  |  |  | 1 | 1.95
AC Pathway | Supports |  |  |  | 1 | 1
AC Pathway | Recepticals |  |  |  | 1 | 40
AC Pathway | Ourdoor Conduit 2 in |  |  |  | 1 | 3
Category | Part Type | Part Manufacturer | Part Number | Part Description | Quantity | Unit Price | Extended Price
AC Cable | #12 - 3 |  |  |  | 1 | 0.85
AC Cable | #10 - 3 |  |  |  | 1 | 1.1
AC Cable | #8 - 3 |  |  |  | 1 | 2.5
AC Cable | #6 - 3 |  |  |  | 1 | 5.5
AC Cable | #2 - 3 |  |  |  | 1 | 11.75
AC Cable | #1 - 3 |  |  |  | 1 | 13.5
Category | Part Type | Part Manufacturer | Part Number | Part Description | Quantity | Unit Price | Extended Price
Fiber | 12 - Plenum |  |  |  | 1 | 0.45
Fiber | 12 - I/O |  |  |  | 1 | 0.7
Category | Part Type | Part Manufacturer | Part Number | Part Description | Quantity | Unit Price | Extended Price
Pathway | J-Hook |  |  |  | 1 | 4.5
Pathway | Innerduct - 2 Duct |  |  |  | 1 | 8.41
Pathway | Conduit - Schedule 40 |  |  |  | 1 | 2
Category | Part Type | Part Manufacturer | Part Number | Part Description | Quantity | Unit Price | Extended Price
Class 2 | Berk Head End |  |  |  | 1 | 2199
Class 2 | Berk PSU |  |  |  | 1 | 899
Class 2 | Berk 4 port Transmitter |  |  |  | 1 | 1385
Class 2 | Berk 4 port remote |  |  |  | 1 | 1385
Class 2 | Berk Cable |  |  | 4 con - 8 fiber | 1 | 5.75

## SoW Template
Labor Rates
MEP Design | 207 | per hour
Electrician | 72 | per hour
Low Voltage | 45 | per hour
Coring | 225 | per core
Trenching | 31 | per foot
Micro Trenching | 13 | per foot
Conduit Installation | 18 | per foot
Cable Installation | 1.5 | per foot
Indoor Installation Scope
|  |  | Labor Cost |  |  |  | Materials |  | Total
Description of Installation |  |  | Units | A/C | Units | CL4 | A/C | CL4 | A/C | CL4
Pre Design | [10 empty] | Notes
| Site Walk / Site Survey | Complete a detailed site walk to review electrical panels in the MDF and IDF locations
| Electrical Panel Audit | Complete a full audit of electrical panels and capacity
Sub Total
Design & Permitting | [10 empty] | Notes
| Power Design | Design a code compliant power system for the MDF and 5 IDF locations
| Plan Check and Review | Provide plans to AHJ for review and approval
| Design Revisions | Assume 1 design revision
| Utilities Locating | Identify utility locations prior to installation
| Permits | Provide required work permits
Sub Total
MDF Installation | [10 empty] | Notes
| Electrical Shutdown | Required shutdown for electrical panel work (Shut down to add circuits to panel)
| Conduit Installation | Installation of conduit and junction boxes from panel to main rack
| Panel Work | Installation of breakers and wiring
| Transformer Installation | Installation of 208v to 480v AC transformer
| Outlet | Install 1 new outlets to the main equipment racks
| PDU | Install and connect PDU's for equipment connectivity
| Cable Installation | Install 10ft #10 AWG Cable
| FMP Head End | Install Transmitter Chassis, Power Supplies, and Transmitter
Sub Total
IDF () - Pathway & Cable Installation | [10 empty] | Notes
| LV Pathway Installation | Install J-Hooks or similar to support Fiber and CL4 Cable
| Conduit Installation | Installation of conduit and junction boxes from panel to main rack
| Receptical Installation | Install twist-lock receptical for PDUs
| CL4 Cable Installation | Install and terminate CL4 cables within the designated pathway
| Fiber Installation | Install 12 Strand SM fiber
| Standard Trenching | Standard trechning for LV cables
| Micro-trenching | Micro trenching for LV cables
| Utility Installation | Trenching for utility power
| Cable Installation | Power cable installation
| Lightining Protection | Install lightning protection at the building egress and the remote location
| Building Entrance Panel | Provide a building entrance panel for AC power at the building egress
| Electrical Panel Installation | Install new electrical panel with breakers
| Coring | Vertical coring include x-ray
| Electrical Shutdown | Complete the required electrical shutdowns to install or modify electrical panels
Sub Total |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
General Installation | [10 empty] | Notes
| Cable Management | General cable management and slack management
| Labeling | Labeling of all cables
| Documentation | Provide asbuilt drawings
| Inspections | Assist with reqwuired inspections and onsite review
Sub Total |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Grand Total |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0

## Trenching Costs (estimated)
Task | Planning avg time (hr/ft) | Planning avg labor cost (ex-materials) $/ft | Planning avg materials cost $/ft | materials (examples)
Micro-trenching (2-duct “flex” with two 1.25″ ducts) | 0.003 (≈20 sec) (calculated) from ~300–1,000 ft/hr production; see sources | $12.0 (calculated) using typical total ~$15/ft less materials below | $2.75 (calculated) = (2 × 1.25″ HDPE @ ~$0.48/ft) + micro-trench grout ~$1–$2/ft + surface seal allowance | 1) Dura-Line 1.25″ SDR-11 HDPE (or FuturePath 2-way) 2) Micro-trench grout/slurry (e.g., Quanta “SuperGrout”) 3) Surface seal/patch (asphalt/cold-patch or mastic) thewaterworkswarehouse.comduraline.com+1Defaultundergroundinfrastructure.com
2″ Class 1 power conduit in trench (PVC Sch 40) | 0.08 (NECA normal conditions) | $3.3–$6.0 (calculated) → 0.08 hr/ft × loaded wage: (a) non-union median ~$41.5/hr ≈ $3.32/ft; (b) higher-burden ~$75/hr ≈ $6/ft | $1.7–$2.5 (calculated) = PVC Sch40 $1.18–$2.41/ft + primer/cement + caution tape allowance | 1) 2″ PVC Sch 40 conduit (bell end) 2) PVC primer & cement 3) Underground warning tape (red “Electric”) Champion FiberglassBureau of Labor Statistics+1elliottelectric.comThe Home Depot+1
HDD (directional boring) 2″ conduit for LV | 0.008 (≈7×10⁻³ hr/ft) typical; slower in adverse soils 0.02–0.03 | $18 (calculated) using municipal bid means ($14–$24/ft) minus materials below | $0.88 (calculated) = 2″ HDPE SDR-11 ~$0.66/ft + 1/2″ 1,250-lb pull tape ~$0.10/ft + #12 tracer wire ~$0.11/ft | 1) 2″ HDPE SDR-11/13.5 conduit 2) 1/2″ 1,250-lb pull tape 3) #12 CCS tracer wire (PE-30) Vermeer Pro tipsCOREMilwaukee CountyCity of De Pere, WisconsinHomeGuidethewaterworkswarehouse.comThe Home Depotgeorgiaunderground.net
HDD (directional boring) 2″ conduit for HV | 0.008 (same bore productivity; separations drive layout, not feet/min) | $14 (calculated) based on bid tabs specifying bored 2″ PVC at ~$14.4–$15/ft, net of materials below | $1.3–$2.4 (calculated) if PVC Sch40 is spec for the pull: conduit $1.18–$2.41/ft + lube allowance | 1) 2″ conduit per spec (many municipal specs show PVC Sch 40 for bored installations) 2) Pulling head/tape 3) Duct lubricant Milwaukee Countyelliottelectric.comThe Home Depot+1
What’s corroborated (2+ sources):
• Micro-trenching width/depth & “~$15/ft” total cost order-of-magnitude; multiple trade articles and vendor brochures agree on high productivity and reduced restoration. duraline.comundergroundinfrastructure.com
• NECA labor units for 2″ PVC (8 man-hours/100 ft). Champion Fiberglass
• HDD daily production near ~1,000 ft/day as a common target, with academic/field literature showing much slower rates in specific soils (≈40 ft/hr). Vermeer Pro tipsCORE
• Municipal bid tabs for bored 2″ conduit cluster between ~$14–$24/ft. Milwaukee CountyCity of De Pere, Wisconsin
(validation notes)
1. Materials unit costs
• 1.25″ HDPE SDR-11 orange: $3,850 per 8,000′ → $0.48/ft (The Waterworks Warehouse). thewaterworkswarehouse.com
• 2″ HDPE SDR-11 orange: $2,650 per 4,000′ → $0.66/ft (same supplier). thewaterworkswarehouse.com
• 2″ PVC Sch40 conduit: retail/distributor spread $1.18–$2.41/ft (Elliott Electric, Home Depot, Lowe’s). elliottelectric.comThe Home Depot+1
• Pull tape 1/2″, 1,250-lb: $311.56/3,000′ → $0.104/ft (Home Depot). The Home Depot
• #12 tracer wire CCS PE-30: $0.113/ft (Georgia Underground). georgiaunderground.net
• Micro-trench grout/slurry: industry articles cite ~$1–$2/ft allowance (process descriptions + cost mentions). For Construction ProsDefault
2. Labor time/productivity.
• NECA labor units (open-cut 2″ PVC): 8 man-hours/100′ → 0.08 hr/ft. Champion Fiberglass
• Micro-trenching production: vendor & trade sources show ~3,000 ft/day (installation) and 35 ft/min cutting; I used a trimmed average to a planning rate of ~300–1,000 ft/hr and set 0.003 hr/ft for estimating. FiberLightCompact Equipment MagazineUtility Contractor Magazine
• HDD production: Vermeer guidance (“if you’re not getting ~1,000 ft/day you’re leaving productivity on the table”) and literature showing ~37.5 ft/hr in sandy soils → I present 0.008 hr/ft typical with a slower bound 0.02–0.03 hr/ft. Vermeer Pro tipsCORE
3. Labor $/ft (burdened).
• BLS median electrician wage ≈ $29.61/hr, with typical burdens ~25–40%+; I used ~40% (BLS ECEC benchmark) → ~$41.5/hr as a non-union national planning rate. Union/high-burden examples push $60–$90/hr; I show sensitivity. 2″ PVC in trench: 0.08 hr/ft × $41.5/hr ≈ $3.32/ft (non-union) to ~$6/ft (higher burden). Bureau of Labor Statistics+1
• For micro-trenching and HDD, market pricing is commonly provided as unit price per foot. I back-solved labor+equipment by subtracting the material basket above from those unit prices, yielding ≈$12/ft (micro-trench from ~$15/ft) and ≈$14–$18/ft (HDD 2″, depending on spec). undergroundinfrastructure.comMilwaukee CountyCity of De Pere, Wisconsin