## Measured Outcomes
Outcomes Comparison
Cost Comparison | Full AC with Standard POE | AC Power mains with FMPS to the desk | AC Power Mains-with FMPS to support POE
| A/C Standard | A/C + FMP | A/C + FMP + POE
AC Power Scope | 234989.467
FMPS and DC Power Scope
POE Scope (LV Scope) | 59092.96
Design & Engineering
Total | 294082.427 | 0 | 0
Savings / Value Comparison
Total cable distances
Cable Gauge
Electrical System Efficiency
Labor Rates
Labor Hours
Smart building performance
Design Time
Project Management Time
Core Space
Conduit Length
Conduit size
Green Certifications
Installation Cost
Maintenance Cost
Permitting Cost
Permitting Time
UPS Cost

## Device Overview
Category | Device Type | Device Detail | Device Natïve Voltage | A/C Power Option | DC Power Option | POE Power Option | Typical Quantity
A/V | AV – Audio | DSP / amplifiers | DC | YES | YES | YES | 5
A/V | AV – Conference | Large flat panels | DC | YES | YES | YES | 14
A/V | AV – Misc | Digital signage | DC | YES | YES | YES | 6
Appliances | Breakroom | Coffee brewers | AC | YES | NO | NO | 3
Appliances | Breakroom | Dishwashers | AC | YES | YES | NO | 2
Appliances | Breakroom | Microwaves | AC | YES | YES | NO | 2.5
Appliances | Breakroom | Refrigerators | AC | YES | YES | NO | 2
Appliances | Breakroom | Vending machines | AC | YES | NO | NO | 3
Appliances | Breakroom | Water coolers | DC | YES | NO | NO | 4
Base Building (Plumbing / HVAC) | HVAC – Terminal | Fan coils | AC | YES | NO | NO | 7
Base Building (Plumbing / HVAC) | HVAC – Terminal | VAV box w/ reheat | AC | YES | NO | NO | 20
Networking | IT – Endpoints | Thin clients | DC | YES | YES | YES | 50
Networking | IT – IDF | Non-PoE switches | DC | YES | YES | NO | 3
Networking | IT – IDF | PoE access switches | DC | YES | YES | NO | 7
Networking | IT – IDF | Rackmount UPS | DC | YES | YES | NO | 4
Networking | IT – IDF | Routers / firewalls | DC | YES | YES | NO | 1.5
Networking | IT – Network Core | Aggregation switch | DC | YES | YES | NO | 1
Life Safety | Life Safety | Fire alarm node | DC | NO | YES | NO | 1
Lighting | Lighting | Emergency inverter | DC | YES | YES | YES | 2
Lighting | Lighting | LED 2x4 troffer | DC | YES | YES | YES | 320
Lighting | Lighting | LED downlights | DC | YES | YES | YES | 80
Office | Outlets | Floor boxes / receptacle strips | DC | YES | NO | NO | 100
Office | Misc Office | Motorized shades | DC | YES | YES | YES | 30
Appliances | Office Equipment | Desktop printers | DC | YES | NO | NO | 10
Appliances | Office Equipment | Floor MFP / copier | DC | YES | NO | NO | 4
Appliances | Office Equipment | Scanners / label printers | DC | YES | NO | NO | 15
Base Building (Plumbing / HVAC) | Plumbing | Exhaust fans | AC | YES | YES | NO | 3
Security | Security | Door controllers | DC | NO | YES | YES | 5
Security | Security | NVR / video server | DC | YES | YES | YES | 2
Security | Security | Security workstations | DC | YES | YES | YES | 3
Office | Sound Masking | Sound Masking Controller/amp | DC | YES | YES | YES | 2
Office | Workstations | Laptop + USB-C dock | DC | YES | YES | YES | 200
Office | Workstations | Task lights (LED) | DC | YES | YES | YES | 150
Office | Workstations | USB/USB-C chargers | DC | YES | YES | YES | 200
A/V | AV – Conference | Video bars / codecs | DC | YES | YES | YES | 13
Lighting | Lighting | LED exit signs | DC | NO | YES | NO | 20
Base Building (Plumbing / HVAC) | Plumbing | Auto faucets/flush valves | DC | YES | YES | NO | 20
A/V | AV – Audio | Ceiling mics/speakers | DC | NO | YES | YES | 50
Base Building (Plumbing / HVAC) | HVAC – Controls | Actuators | AC | YES | YES | NO | 30
Base Building (Plumbing / HVAC) | HVAC – Controls | Thermostats | AC | YES | YES | YES | 25
Life Safety | Life Safety | Detectors | DC | NO | YES | NO | 60
Life Safety | Life Safety | Pull stations/modules | DC | NO | YES | NO | 15
Life Safety | Life Safety | Speakers/strobes | DC | NO | YES | YES | 70
Office | Misc Office | Occupancy/daylight sensors | DC | NO | YES | YES | 80
Security | Security | Maglocks / strikes | DC | NO | YES | NO | 35
Office | Sound Masking | Sound Masking Emitters | DC | NO | YES | YES | 200
Office | Workstations | LCD monitor | DC | YES | YES | YES | 400
Networking | IT – Wireless | Wi‑Fi access points | DC | NO | NO | YES | 22
Security | Security | Fixed IP cameras | DC | NO | YES | YES | 25
Security | Security | PTZ cameras | DC | NO | YES | YES | 3
Networking | Workstations | IP phone | DC | YES | YES | YES | 200
Base Building (Plumbing / HVAC)
Elecrical
Networking
Lighting
A/V
Security
Office
Appliances
Life Safety

## Full Build MEP Scope
Phase Summary
Phase | Steps | First_Step | Last_Step
0) Project Setup / Contract Admin (Pre-Design) | 5 | 1 | 5
1) Existing Conditions / Field Investigation | 5 | 6 | 10
2) Schematic Design (SD) – Concept + Basis of Design | 8 | 11 | 18
3) Design Development (DD) – Engineering + Coordination | 8 | 19 | 26
4) Construction Documents (CD) – Permit/Bid Set | 8 | 27 | 34
5) Permitting / Authority Review | 3 | 35 | 37
6) Bidding / Procurement Support (Hard Bid) | 4 | 38 | 41
7) Construction Administration (CA) | 9 | 42 | 50
8) Commissioning / Closeout (if in MEP scope) | 5 | 51 | 55
9) Optional / Additional Services (Explicit Adders) | 7 | 56 | 62
MEP Engineer Scope of Work – Line-Item Work Breakdown Structure
Phase 0 - Project Setup | Line Item |  | Details
1 | Confirm basis of design inputs |  | Program, occupancy/use, hours of operation; tenant/landlord responsibilities; utility info; existing as-builts
2 | Define codes + standards |  | Applicable codes; local amendments; AHJ preferences
3 | Kickoff + execution plan |  | Schedule/milestones; deliverables; communication plan; RFI workflow; review cycles
4 | MEP scope boundaries |  | By MEP vs architect/structural/GC/trades; low-voltage, fire alarm, controls, TAB, commissioning roles
5 | Fee assumptions + exclusions |  | Document inclusions/exclusions; additional services triggers
Phase 1 - Existing Conditions / Field Investigation | Line Item |  | Details
6 | Site walk + documentation |  | Verify MEP rooms, shafts, ceiling plenums, routes
7 | Survey of existing systems (if renovation) |  | Equipment inventory; nameplate data; panel schedules; piping sizes
8 | Utility verification |  | Electrical service/voltage; gas; domestic water; sanitary; storm
9 | Deficiency log / risk register |  | Capacity shortfalls; code issues; access/clearance constraints
10 | Existing load/capacity analysis |  | Electrical spare capacity; HVAC capacity vs tenant loads; plumbing demand capacity
Phase 2 - Existing Conditions / Field Investigation | Line Item |  | Details
11 | Define design criteria (BOD) |  | Temperature, ventilation rates, lighting levels, power densities
12 | Preliminary load calculations |  | HVAC block loads; electrical load summary; plumbing fixture counts + demand
13 | System selection / narratives |  | Mechanical system type; electrical distribution concept; plumbing approach
14 | Space planning requirements |  | MEP room sizing; service clearances; access
15 | Preliminary riser/pathway concepts |  | Shafts, risers, major conduit/piping routes
16 | SD drawings (as applicable) |  | Concept one-lines; key plans; preliminary layouts
17 | SD coordination |  | Flag major clashes/space constraints
18 | SD cost/scope alignment support |  | Provide allowances/quantities for early estimating
Phase 3 - Design Development (DD) – Engineering + Coordination | Line Item |  | Details
19 | Refined calculations |  | Room-by-room loads; ventilation/exhaust; electrical panel loads; preliminary fault current; plumbing sizing
20 | Equipment selection |  | Mechanical equipment schedules; electrical gear selection; plumbing equipment selection
21 | Controls concept |  | Sequences of operation; points list (as applicable)
22 | Lighting + controls design |  | Fixture layout strategy; control zoning; daylight/occupancy logic
23 | Distribution design |  | Duct/piping sizing + routing; feeder/branching; plumbing mains/branches and venting
24 | Interdisciplinary coordination |  | Ceiling coordination; draft sleeve/openings list; fire-rated penetration strategy
25 | DD deliverables |  | Updated drawings; risers/diagrams; schedules; outline specs
26 | DD QA/QC review |  | Internal checks for coordination, code compliance, constructability
Phase 4 - Construction Documents (CD) – Permit/Bid Set | Line Item |  | Details
27 | Final engineering calculations |  | Finalize HVAC; electrical load calcs + schedules; protection/coordination intent; plumbing sizing
28 | Final plans and details |  | Mechanical plans/risers/details; electrical plans/one-lines/schedules; plumbing plans/risers/details
29 | Specifications (Div 22/23/26 ± 27/28) |  | Performance, products, execution, testing
30 | Equipment and device coordination |  | Connections (voltage/MCA/MOCP/BTU/flows); access/clearances
31 | Final sleeve/penetration documentation |  | Sleeve plans; opening sizes; firestopping requirements
32 | Bid alternates / options (if required) |  | Define add/deduct scopes
33 | Engineer’s estimate support (optional) |  | Quantity support / clarifications for estimator
34 | CD QA/QC + stamping |  | Discipline lead review; code checklist; seal/stamp where required
Phase 5 - Permitting / Authority Review | Line Item |  | Details
35 | Permit application support |  | Forms; energy compliance documentation; calculations package
36 | Plan review comment responses |  | Written responses; drawing revisions
37 | Resubmittals |  | Updated sheets; revision tracking; final approvals
Phase 6 - Bidding / Procurement Support (Hard Bid) | Line Item |  | Details
38 | Issue for bid |  | Addenda coordination
39 | Bidder RFIs |  | Written responses; addenda as needed
40 | Bid walkthrough support (optional) |  | Attend walkthrough; capture questions
41 | Bid leveling support (optional) |  | Clarify scope gaps; alternates; substitutions
Phase 7 - Construction Administration (CA) | Line Item |  | Details
42 | Submittal review |  | Equipment, fixtures, controls, panels, valves, dampers, etc.
43 | RFI responses |  | Respond, document, and track
44 | Shop/coordination drawing review |  | Major routing, clearances, conflicts
45 | Site visits (periodic) |  | Progress observations; field reports
46 | Change management |  | Evaluate change proposals; CCD/ASI as needed
47 | Field issue resolution |  | Constructability conflicts; unforeseen conditions
48 | Testing witness support (as required) |  | Observe start-up / acceptance testing as specified
49 | As-built review |  | Record drawings and O&M completeness
50 | Punchlist support |  | Create/verify MEP punchlist and closeout
Phase 8 - Commissioning / Closeout (if in MEP scope) | Line Item |  | Details
51 | Commissioning plan support |  | Support Cx plan and roles
52 | Functional performance testing support |  | Participate in FPT; document results
53 | TAB coordination and review (mechanical) |  | Coordinate TAB; review reports
54 | Training sessions |  | Owner training on systems/controls
55 | Final closeout |  | O&M acceptance; warranties list; final sign-offs
Phase 9 - Optional | Line Item |  | Details
56 | Arc flash study / protective device coordination / selective coordination |  | Only if authorized; define deliverables and fee
57 | BIM modeling (LOD 300/350) + clash resolution |  | Only if authorized; define deliverables and fee
58 | Detailed cost estimating / value engineering workshops |  | Only if authorized; define deliverables and fee
59 | Shutdown planning / after-hours phasing for occupied buildings |  | Only if authorized; define deliverables and fee
60 | Enhanced commissioning / M&V (measurement & verification) |  | Only if authorized; define deliverables and fee
61 | LEED/WELL documentation support |  | Only if authorized; define deliverables and fee
62 | Low-voltage (Div 27/28) design and/or delegated fire alarm design |  | Only if authorized; define deliverables and fee

## Installation Scope AC
Labor Role | Avg Rate ($/hr) | Formula
Electrician | 43.9 | 43.9
Project Manager / Construction Manager | 51.43 | 51.43
Electrical Designer / Drafter | 35.44 | 35.44
Construction Laborer | 22.47 | 22.47
Low-Voltage / Fire Alarm Tech | 28.51 | 28.51
Sample Scope | Description of Installation | Quantity | Unit | Labor Units (hrs/unit) | Labor Hours | Labor Rate ($/hr) | Labor Total | Material Unit Cost ($) | Material Total | Line Item Total | Notes | Milestone | Labor Type
1) Preconstruction / Admin
Labor | Kickoff meeting, confirm scope boundaries, coordination plan | 1 | lot | 4 | 4 | 51.43 | 205.72 |  |  | 205.72 | Include trade coordination cadence | Kickoff complete | Project Manager / Construction Manager
Labor | Site walk / existing conditions verification | 1 | lot | 6 | 6 | 51.43 | 308.58 |  |  | 308.58 | Verify routes, core needs, clearances | Site walk complete | Project Manager / Construction Manager
Labor | Submittals & procurement log (panels, transformer, fixtures, controls) | 1 | lot | 10 | 10 | 28.51 | 285.1 |  |  | 285.1 | Submittals, review cycles | Submittals approved | Low-Voltage / Fire Alarm Tech
Labor | BIM/coordination drawings (if required) | 1 | lot | 16 | 16 | 35.44 | 567.04 |  |  | 567.04 | Only if contract requires | Coordination model complete | Electrical Designer / Drafter
Labor | Mobilization, safety plan, daily cleanup/housekeeping | 1 | lot | 12 | 12 | 51.43 | 617.16 |  |  | 617.16 | Project admin allowance | Mobilization complete | Project Manager / Construction Manager
2) Permitting
Labor | Provide all necessary electrical permits / coordinate inspections | 1 | lot | 8 | 8 | 51.43 | 411.44 |  |  | 411.44 | Fees by others unless stated | Permit issued | Project Manager / Construction Manager
Material | Permit fees (allowance) | 1 | lot |  |  |  |  | 500 | 500 | 500 | Enter actual fees | Permit fees paid
3) MER → Tenant Floor (Primary Distribution)
Labor and Materials | Provide/install feeder breaker in MER gear (size/series per gear) | 1 | ea | 6 | 6 | 43.9 | 263.4 | 2500 | 2500 | 2763.4 | Confirm spare space; verify AIC | Breaker installed | Electrician
Labor and Materials | Install feeder conduit from MER through central riser to tenant floor (e.g., 4" EMT/IMC) | 174 | ft | 0.18 | 31.32 | 43.9 | 1374.948 | 18 | 3132 | 4506.948 | Distance includes vertical + horizontal + waste | Feeder conduit complete | Electrician
Labor and Materials | Install feeder conductors (3P+N+G) in feeder conduit | 174 | ft | 0.12 | 20.88 | 43.9 | 916.632 | 18 | 3132 | 4048.632 | Conductor size to be engineered/confirmed | Feeder conductors pulled | Electrician
Labor and Materials | Install pull boxes / junction cabinets along route | 4 | ea | 1.75 | 7 | 43.9 | 307.3 | 250 | 1000 | 1307.3 | As required by bend/length limits | Pull boxes installed | Electrician
Labor and Materials | Core drill penetrations for feeder pathway (if required) | 6 | ea | 1.25 | 7.5 | 22.47 | 168.525 | 50 | 300 | 468.525 | Confirm if sleeves exist / who cores | Cores complete | Construction Laborer
Labor and Materials | Firestop penetrations (UL listed system) | 6 | ea | 0.35 | 2.1 | 22.47 | 47.187 | 25 | 150 | 197.187 | Clarify responsibility | Firestopping complete | Construction Laborer
Labor | Terminate feeder at MER gear | 1 | end | 4 | 4 | 43.9 | 175.6 |  |  | 175.6 | Torque per manufacturer | MER termination complete | Electrician
Labor | Terminate feeder at tenant main panel | 1 | end | 4 | 4 | 43.9 | 175.6 |  |  | 175.6 | Torque per manufacturer | Tenant termination complete | Electrician
Labor and Materials | Grounding and bonding for feeder/conduit | 1 | lot | 4 | 4 | 43.9 | 175.6 | 200 | 200 | 375.6 | Bushings, jumpers, ground bar as needed | Grounding complete | Electrician
Labor and Materials | Label feeder, pull boxes, panels per labeling standard | 1 | lot | 3 | 3 | 43.9 | 131.7 | 250 | 250 | 381.7 | Panel directories included elsewhere | Labeling complete | Electrician
4) Tenant Electrical Room – Main Distribution & Step-Down
Labor and Materials | Provide/install tenant main panelboard 480/277V (400A class) | 1 | ea | 10 | 10 | 43.9 | 439 | 2500 | 2500 | 2939 | Main breaker or MLO; coordinate AIC | Main panel set | Electrician
Labor and Materials | Provide/install dry-type transformer 480→208/120 (kVA per final calc) | 1 | ea | 16 | 16 | 43.9 | 702.4 | 4500 | 4500 | 5202.4 | Include vibration pads if required | Transformer set | Electrician
Labor and Materials | Provide/install lighting panelboard 277V (225A class) | 1 | ea | 10 | 10 | 43.9 | 439 | 1200 | 1200 | 1639 | Feeds lighting + emergency inverter | Lighting panel set | Electrician
Labor and Materials | Provide/install mechanical panelboard 480/277V (225A class) | 1 | ea | 10 | 10 | 43.9 | 439 | 1200 | 1200 | 1639 | Feeds HVAC loads as needed | Mech panel set | Electrician
Labor and Materials | Provide/install power panelboard PP-1 208/120V (225A class) | 1 | ea | 10 | 10 | 43.9 | 439 | 1200 | 1200 | 1639 | General receptacles + equipment | PP-1 set | Electrician
Labor and Materials | Provide/install power panelboard PP-2 208/120V (225A class) | 1 | ea | 10 | 10 | 43.9 | 439 | 1200 | 1200 | 1639 | Conference/AV/IT + spare | PP-2 set | Electrician
Labor and Materials | Install feeder: main panel → transformer (primary) | 60 | ft | 0.22 | 13.2 | 43.9 | 579.48 | 15 | 900 | 1479.48 | Conduit+wire allowance; adjust after layout | Primary xfmr feeder complete | Electrician
Labor and Materials | Install feeder: transformer → PP panels (secondary) | 120 | ft | 0.2 | 24 | 43.9 | 1053.6 | 12 | 1440 | 2493.6 | Conduit+wire allowance; adjust after layout | Secondary feeders complete | Electrician
Labor and Materials | Install feeder: main panel → lighting panel | 60 | ft | 0.18 | 10.8 | 43.9 | 474.12 | 12 | 720 | 1194.12 | Allowance | Lighting panel feeder complete | Electrician
Labor and Materials | Install feeder: main panel → mechanical panel | 60 | ft | 0.18 | 10.8 | 43.9 | 474.12 | 12 | 720 | 1194.12 | Allowance | Mech panel feeder complete | Electrician
Labor and Materials | Panel schedules / circuit directories | 1 | lot | 6 | 6 | 35.44 | 212.64 |  | 0 | 212.64 | Final typed directories | Directories complete | Electrical Designer / Drafter
5) Lighting (277V) – Fixtures, Branching, Controls
Material | Provide LED 2x4 troffer fixtures | 320 | ea |  |  |  |  | 95 | 30400 | 30400 | Fixture schedule governs | Fixtures delivered
Labor | Install LED 2x4 troffer fixtures | 320 | ea | 0.5 | 160 | 43.9 | 7024 |  | 0 | 7024 | Mount, connect, aim/level | Troffers installed | Electrician
Material | Provide LED downlight fixtures | 80 | ea |  |  |  |  | 60 | 4800 | 4800 | Fixture schedule governs | Downlights delivered
Labor | Install LED downlight fixtures | 80 | ea | 0.6 | 48 | 43.9 | 2107.2 |  | 0 | 2107.2 | Cut-in/rough-in varies | Downlights installed | Electrician
Material | Provide LED exit signs (battery) | 20 | ea |  |  |  |  | 45 | 900 | 900 | Coordinate egress locations | Exit signs delivered
Labor | Install LED exit signs | 20 | ea | 0.5 | 10 | 43.9 | 439 |  | 0 | 439 | Mount and connect | Exit signs installed | Electrician
Material | Provide emergency inverter units | 2 | ea |  |  |  |  | 5000 | 10000 | 10000 | As specified | Inverters delivered
Labor | Install emergency inverter units | 2 | ea | 8 | 16 | 43.9 | 702.4 |  | 0 | 702.4 | Mount, connect, test | Inverters installed | Electrician
Labor and Materials | Install lighting branch wiring (MC cable whips/homers) | 4900 | ft | 0.02 | 98 | 43.9 | 4302.2 | 1.5 | 7350 | 11652.2 | Lengths are allowance; adjust with plan | Lighting rough-in complete | Electrician
Material | Provide occupancy/daylight sensors | 80 | ea |  |  |  |  | 40 | 3200 | 3200 | Per lighting controls design | Sensors delivered
Labor | Install occupancy/daylight sensors | 80 | ea | 0.45 | 36 | 43.9 | 1580.4 |  | 0 | 1580.4 | Mount + wire | Sensors installed | Electrician
Material | Provide lighting controls system hardware (panels/gateways/relays) | 1 | lot |  |  |  |  | 8000 | 8000 | 8000 | System-specific; may be by controls vendor | Controls hardware delivered
Labor | Controls integration, addressing, functional test | 1 | lot | 24 | 24 | 28.51 | 684.24 |  |  | 684.24 | Commissioning support | Lighting controls commissioned | Low-Voltage / Fire Alarm Tech
6) General Power (208/120V) – Floor Boxes, Receptacles, Branch Circuits
Material | Provide floor box assemblies (box + trim + cover) | 100 | ea |  |  |  |  | 120 | 12000 | 12000 | Coordinate with furniture/layout | Floor boxes delivered
Labor | Rough-in floor boxes | 100 | ea | 1.1 | 110 | 43.9 | 4829 |  |  | 4829 | Coordinate with floor system | Floor box rough-in complete | Electrician
Labor | Trim-out floor boxes | 100 | ea | 0.55 | 55 | 43.9 | 2414.5 |  |  | 2414.5 | Devices/plates | Floor box trim complete | Electrician
Material | Provide duplex receptacles for floor boxes (2 per floor box) | 200 | ea |  |  |  |  | 5 | 1000 | 1000 | Commercial grade | Floor receptacles delivered
Labor | Install duplex receptacles for floor boxes | 200 | ea | 0.35 | 70 | 43.9 | 3073 |  |  | 3073 | Terminate and test | Floor receptacles installed | Electrician
Material | Provide wall duplex receptacles | 150 | ea |  |  |  |  | 4 | 600 | 600 | Commercial grade | Wall receptacles delivered
Labor | Install wall duplex receptacles | 150 | ea | 0.35 | 52.5 | 43.9 | 2304.75 |  |  | 2304.75 | Terminate and test | Wall receptacles installed | Electrician
Labor and Materials | Install branch conduit (e.g., 3/4" EMT) for receptacles + dedicated circuits | 8040 | ft | 0.085 | 683.4 | 43.9 | 30001.26 | 0.9 | 7236 | 37237.26 | Allowance; refine with takeoff | Branch conduit complete | Electrician
Labor and Materials | Install branch conductors (#12 equiv. hot/neutral/ground) | 24120 | ft | 0.03 | 723.6 | 43.9 | 31766.04 | 0.25 | 6030 | 37796.04 | Allowance; refine with takeoff | Branch wiring complete | Electrician
Labor and Materials | Install 20A 1-pole breakers in PP panels | 161 | ea | 0.15 | 24.15 | 43.9 | 1060.185 | 12 | 1932 | 2992.185 | Proxy count; adjust after circuiting | Breakers installed | Electrician
Labor and Materials | Install 30A 2-pole breakers in PP panels | 10 | ea | 0.15 | 1.5 | 43.9 | 65.85 | 30 | 300 | 365.85 | For 208V dedicated loads | Dedicated breakers installed | Electrician
7) Mechanical/Plumbing Power (480/277V) – Connections
Labor and Materials | Provide/install disconnect switches for exhaust fans | 3 | ea | 0.75 | 2.25 | 43.9 | 98.775 | 120 | 360 | 458.775 | As required by code/location | Exhaust disconnects installed | Electrician
Labor and Materials | Provide/install disconnect switches for fan coil units | 7 | ea | 0.75 | 5.25 | 43.9 | 230.475 | 120 | 840 | 1070.475 | If not factory provided | FCU disconnects installed | Electrician
Labor and Materials | Branch conduit/wire to VAVs, fan coils, exhaust fans (allowance) | 1800 | ft | 0.05 | 90 | 43.9 | 3951 | 0.9 | 1620 | 5571 | Refine with equipment plan | Mech rough-in complete | Electrician
8) Testing, Energization, Closeout
Labor | Megger/insulation testing of feeders and critical circuits | 1 | lot | 12 | 12 | 43.9 | 526.8 |  |  | 526.8 | Include reports as required | Testing complete | Electrician
Labor | Torque verification of terminations + labeling | 1 | lot | 8 | 8 | 43.9 | 351.2 |  |  | 351.2 | Torque log if required | Torque/labels complete | Electrician
Labor | Functional verification: lighting controls + emergency inverter | 1 | lot | 10 | 10 | 28.51 | 285.1 |  |  | 285.1 | Coordinate witness testing | Functional tests complete | Low-Voltage / Fire Alarm Tech
Labor | As-builts (redlines) + O&M manuals compilation support | 1 | lot | 18 | 18 | 51.43 | 925.74 |  |  | 925.74 | Closeout package | As-builts/O&M complete | Project Manager / Construction Manager
Labor | Owner training session support | 1 | lot | 6 | 6 | 51.43 | 308.58 |  |  | 308.58 | Systems overview | Training complete | Project Manager / Construction Manager
Labor | Punchlist corrections + final walk | 1 | lot | 16 | 16 | 51.43 | 822.88 |  |  | 822.88 | Allowance | Punchlist closed | Project Manager / Construction Manager
TOTAL | [6 empty] | 111677.467 |  | 123312 | 234989.467

## Installation Scope LV
Labor Role | Avg Rate ($/hr)
Project Manager / Construction Manager | 51.43 | 51.43
Low Voltage Technician | 30.77 | 30.77
Fiber Technician / Splicer | 33.9 | 33.9
Network & Systems Administrator | 46.54 | 46.54
Sample Scope | Description of Installation | Quantity | Unit | Labor Units (hrs/unit) | Labor Hours | Labor Rate ($/hr) | Labor Total | Material Part # | Material Unit Cost ($) | Material Total | Line Item Total | Notes | Milestone | Labor Role
1) Preconstruction / Admin
Labor | Kickoff meeting, confirm scope boundaries, coordination plan | 1 | lot | 4 | 4 | 51.43 | 205.72 |  |  |  | 205.72 | Coordination cadence + comms plan | Kickoff complete | Project Manager / Construction Manager
Labor | Site survey / walkdown (IDF/MDF locations, pathways, ceiling conditions) | 1 | lot | 6 | 6 | 30.77 | 184.62 |  |  |  | 184.62 | Verify routes, firestop needs, access windows | Site survey complete | Low Voltage Technician
Labor | Labeling standard + cable schedule + port map (draft) | 1 | lot | 8 | 8 | 46.54 | 372.32 |  |  |  | 372.32 | Defines label format, rack elevations, patching plan | Labeling plan complete | Network & Systems Administrator
Labor | Submittals & procurement log (cable, racks, panels, jacks, patch cords) | 1 | lot | 8 | 8 | 51.43 | 411.44 |  |  |  | 411.44 | Track lead times | Submittals approved | Project Manager / Construction Manager
Labor | Mobilization, safety plan, staging, daily housekeeping | 1 | lot | 8 | 8 | 51.43 | 411.44 |  |  |  | 411.44 | Project admin allowance | Mobilization complete | Project Manager / Construction Manager
2) Pathways & Support
Labor and Materials | Provide/install J-hooks and supports for horizontal cabling | 300 | ea | 0.05 | 15 | 30.77 | 461.55 | JHOOK-2IN | 2.5 | 750 | 1211.55 | Spacing per code/manufacturer | J-hooks installed | Low Voltage Technician
Labor and Materials | Provide/install cable tray (12") sections including fittings | 200 | ft | 0.08 | 16 | 30.77 | 492.32 | TRAY-12IN | 20 | 4000 | 4492.32 | Includes splice kits/hardware | Cable tray complete | Low Voltage Technician
Labor and Materials | Core drill + sleeve LV penetrations (as required) | 20 | ea | 0.75 | 15 | 30.77 | 461.55 | LV-SLEEVE-4IN | 35 | 700 | 1161.55 | Coordinate with GC for coring responsibility | Penetrations complete | Low Voltage Technician
Labor and Materials | Firestop LV penetrations (UL listed system) | 50 | ea | 0.3 | 15 | 30.77 | 461.55 | FIRESTOP-KIT | 25 | 1250 | 1711.55 | UL system per wall type | Firestopping complete | Low Voltage Technician
3) MDF/IDF Buildout (Racks, Backboards, Grounding)
Labor and Materials | Provide/install 2-post floor rack (7 ft) incl. anchoring | 3 | ea | 3 | 9 | 30.77 | 276.93 | RACK-2POST-7FT | 350 | 1050 | 1326.93 | For MDF + IDFs | Racks installed | Low Voltage Technician
Labor and Materials | Provide/install wall-mount cabinet (12U) for remote IDF (if needed) | 2 | ea | 4 | 8 | 30.77 | 246.16 | CAB-12U | 900 | 1800 | 2046.16 | Optional based on design | Cabinets installed | Low Voltage Technician
Labor and Materials | Provide/install ladder rack above racks (12") | 60 | ft | 0.15 | 9 | 30.77 | 276.93 | LADDER-12IN | 18 | 1080 | 1356.93 | Includes brackets/couplers | Ladder rack complete | Low Voltage Technician
Material | Provide vertical cable managers (7 ft) | 6 | ea |  |  |  |  | VERT-MGR-7FT | 120 | 720 | 720 | Qty varies by rack count
Labor | Install vertical cable managers | 6 | ea | 0.5 | 3 | 30.77 | 92.31 |  |  |  | 92.31 | Mount to racks |  | Low Voltage Technician
Material | Provide Cat6 48-port patch panels | 12 | ea |  |  |  |  | PATCHPANEL-CAT6-48P | 110 | 1320 | 1320 | MDF/IDF total ports allowance
Labor | Install Cat6 patch panels in racks | 12 | ea | 0.75 | 9 | 30.77 | 276.93 |  | 0 | 0 | 276.93 | Includes dressing/hardware |  | Low Voltage Technician
Material | Provide Cat6 keystone jacks | 500 | ea |  |  |  |  | JACK-CAT6 | 3.5 | 1750 | 1750
Material | Provide 2-port faceplates | 250 | ea |  |  |  |  | FACEPLATE-2P | 1.75 | 437.5 | 437.5
Material | Provide cable label kit (thermal labels + wrap) | 1 | lot |  |  |  |  | LABEL-KIT | 250 | 250 | 250
Labor and Materials | Grounding/bonding for racks (busbar, lugs, bond jumpers) | 1 | lot | 4 | 4 | 30.77 | 123.08 | RACK-GND-KIT | 300 | 300 | 423.08 |  | Grounding complete | Low Voltage Technician
4) Horizontal Cabling (Cat6)
Material | Provide Cat6 plenum cable (1000 ft boxes) | 20 | box |  |  |  |  | CAT6-PLENUM-1000FT | 230 | 4600 | 4600 | Qty depends on cable lengths
Labor | Pull & terminate Cat6 drops (2 cables per outlet) incl. patch panel + work area | 250 | outlet | 2 | 500 | 30.77 | 15385 |  |  |  | 15385 | Includes dressing, testing prep | Horizontal cabling installed | Low Voltage Technician
Material | Provide Cat6 patch cords 7 ft (user side) | 250 | ea |  |  |  |  | PATCHCORD-CAT6-7FT | 6 | 1500 | 1500
Material | Provide Cat6 patch cords 3 ft (rack side) | 250 | ea |  |  |  |  | PATCHCORD-CAT6-3FT | 4 | 1000 | 1000
5) Wireless (Wi-Fi) & Specialty Drops
Labor | Install Wi-Fi AP Cat6 drops (home run to IDF) | 20 | ea | 1.5 | 30 | 30.77 | 923.1 |  |  |  | 923.1 | Ceiling locations per plan | AP drops complete | Low Voltage Technician
Material | Provide AP mounting brackets (if required) | 20 | ea |  |  |  | 0 | WAP-BRKT | 25 | 500 | 500
6) Fiber Backbone (MDF↔IDF)
Labor and Materials | Provide/install OM4 12-strand fiber trunk between MDF and IDFs | 2 | run | 6 | 12 | 33.9 | 406.8 | FIBER-OM4-12S | 900 | 1800 | 2206.8 | Length/spec to be confirmed | Fiber trunks installed | Fiber Technician / Splicer
Material | Provide fiber enclosure/panel (rack mount) with LC adapters | 4 | ea |  |  |  |  | FIBER-PANEL-LC | 250 | 1000 | 1000
Labor | Terminate fiber (LC) at panels (pigtail+splice) | 48 | term | 0.5 | 24 | 33.9 | 813.6 |  |  |  | 813.6 | 12-strand x 2 ends x 2 runs |  | Fiber Technician / Splicer
Material | Provide OM4 LC pigtails | 48 | ea |  |  |  |  | PIGTAIL-LC-OM4 | 8 | 384 | 384
7) Testing, Certification, Closeout
Labor | Test & certify Cat6 links (Fluke reports) | 520 | link | 0.05 | 26 | 30.77 | 800.02 |  | 0 | 0 | 800.02 | Includes outlets + APs + spares | Testing complete | Low Voltage Technician
Labor | Compile test results + as-builts + rack elevations | 1 | lot | 12 | 12 | 46.54 | 558.48 |  | 0 | 0 | 558.48 | Deliver PDF/CSV | As-builts delivered | Network & Systems Administrator
Labor | Owner/IT turnover meeting + labeling walkdown | 1 | lot | 4 | 4 | 51.43 | 205.72 |  | 0 | 0 | 205.72 |  | Turnover complete | Project Manager / Construction Manager
Optional / Adders (if in scope)
Labor and Materials | Install IP cameras incl. Cat6 drop + mounting (allowance) | 10 | ea | 2.5 | 25 | 30.77 | 769.25 | CAM-POE-TBD | 250 | 2500 | 3269.25 | Camera model by owner |  | Low Voltage Technician
Labor and Materials | Install access control door hardware + cabling (allowance) | 8 | door | 4 | 32 | 30.77 | 984.64 | AC-DOOR-KIT-TBD | 600 | 4800 | 5784.64 | Controller/readers by owner |  | Low Voltage Technician
TOTAL | [6 empty] | 25601.46 |  |  | 33491.5 | 59092.96

## Sheet2
A/C Parts | Low Voltage Parts
Material Part #
JHOOK-2IN
TRAY-12IN
LV-SLEEVE-4IN
FIRESTOP-KIT
RACK-2POST-7FT
CAB-12U
LADDER-12IN
VERT-MGR-7FT
PATCHPANEL-CAT6-48P
JACK-CAT6
FACEPLATE-2P
LABEL-KIT
RACK-GND-KIT
CAT6-PLENUM-1000FT
PATCHCORD-CAT6-7FT
PATCHCORD-CAT6-3FT
WAP-BRKT
FIBER-OM4-12S
FIBER-PANEL-LC
PIGTAIL-LC-OM4
CAM-POE-TBD
AC-DOOR-KIT-TBD